## PROJ
ID | D20
Name | B.E.A. GENERATING STATION
Location | Fleetwood, Lancashire
Year | 1951
Remarks
Reference Level | 0
Level Source | Figure of BH31 (in load-time-settlement graph) given in mAOD
Groundwater depth
Reference | Solera SA (2018) Personal communication

## LOCA
Hole ID | Easting (X) | Northing (Y) | Ground Level (Z) | Final depth | Co-ordinate Source | Location Remarks
LOCA_ID | LOCA_NATE | LOCA_NATN | LOCA_GL | LOCA_FDEP | LOCA_SOU | LOCA_REM
ID | m | m | m | m
SITE | 333690 | 446718 | 6.55
BH31 |  |  | 6.55 |  |  | 27.5 m from pile 21A
21A |  |  | 6.55
21B |  |  | 6.55

## GEOL
Hole ID | Top Depth | Base Depth | Legend code | Geology code | General description of stratum
LOCA_ID | GEOL_TOP | GEOL_BASE | GEOL_LEG | GEOL_GEOL | GEOL_DESC
ID | m | m
21A | 0 | 2.4383 | 103 | MGR | Fill of ashes
21A | 2.4383 | 2.8955 | 201 | TFD | Clay
21A | 2.8955 | 3.8098 | 401 | TFD | Fine sand
21A | 3.8098 | 5.029 | 430 | TFD | Sand and gravel
21A | 5.029 | 6.5529 | 501 | TFD | Coarse gravel
21A | 6.5529 | 8.6864 | 401 | TFD | Sand
21A | 8.6864 | 10.8199 | 430 | TFD | Rounded gravel
21A | 10.8199 | 11.5818 | 202 | TFD | Silty clay
21A | 11.5818 | 15 | 401 | TFD | Medium sand
21B | 0 | 1.7 | 102 | MGR | Made ground
21B | 1.7 | 2 | 201 | TFD | Clay
21B | 2 | 2.5 | 203 | TFD | Sandy clay
21B | 2.5 | 6 | 103 | TFD | Sandy ballast
21B | 6 | 8 | 401 | TFD | Coarse Sand
21B | 8 | 9.15 | 102 | TFD | Coarse Ballast

## LLPL
Hole ID | Top Depth | Moisture Content | Liquid Limit | Plastic Limit | Plasticity Index | Percentage passing | Specimen Description
LOCA_ID | SAMP_TOP | LLPL_MC | LLPL_LL | LLPL_PL | LLPL_PI | LLPL_425 | SPEC_DESC
ID | m | % | % | % | % | %

## ISPT
Hole ID | Test Depth | Corrected | N Value
LOCA_ID | ISPT_TOP | ISPT_CORR | ISPT_SPTN
m

## TRIG
BH ID | Top Depth | Sample Ref | Test Type | Sample Condition | Specimen Diameter | Undrained shear strength at failure | Remarks
LOCA_ID | SAMP_TOP | SAMP_REF | TRIG_TYPE | TRIG_COND | TRIT_SDIA | TRIT_CU | TRIG_REM
ID | m |  |  |  | mm | kPa

## CULN
BH ID | Trend Description | z0 definition | Gradient | Intercept
LOCA_ID | CULN_NAME | CULN_ZDEF | CULN_EQU1 | CULN_EQU2
ID |  | m | kPa/m | kPa

## CONS
BH ID | Top Depth | Sample Ref | Sample Condition | Coefficient of volume compressibility | Coefficient of consolidation
LOCA_ID | SAMP_TOP | SAMP_REF | CONS_COND | CONS_INMV | CONS_CVRT
ID | m |  |  | m²/MN | m²/yr

## WSTG
Hole ID | Depth to water strike | Remarks
LOCA_ID | WSTG_DPTH | WSTG_REM
ID | m

## PIEZ
BH ID | Top Depth | Sample Ref | Piezometric Head
LOCA_ID | SAMP_TOP | SAMP_REF | PIEZ_HEAD
ID | m |  | m

## PILE
Pile ID | Pile Material | Pile Type/Installation Method | Total Time to Install | Ground Level (Z) | Pile Length | Upstand | Cut-off-level (C.O.L) | Pile Base Level | Casing Base Depth | Casing Type | Pile Shaft Circumference | Pile Shaft Area | Pile Base Area | Pile Shape | Pile Key Dimension | Pile Base Dimension | Pile Undeream Height | Pile Wall Thickness | Working or test pile | Rake (1:n from vertical) | Design Working Load | Design Verification Load (DVL) | Concrete mix designation | Concrete strength class | Concrete design class | Supprt fluid type | Pile Cap Details | Pile Remarks
PILE_ID | PILE_CON | PILE_INST | PILE_TIM | PILE_GL | PILE_LEN | PILE_UPS | PILE_CUT | PILE_BASE | PILE_SLVD | PILE_CAS | PILE_CIRC | PILE_ASH | PILE_ABS | PILE_SHAP | PILE_DIM | PILE_BDIM | PILE_UNDH | PILE_THCK | PILE_PURP | PILE_RAKE | PILE_DSWL | PILE_DVL | PILE_CDES | PILE_CSTR | PILE_CDC | PILE_FYTP | PILE_CAP | PILE_REM
ID |  |  | Days | m | m | m | m | m | m |  | m | m² | m² |  | m | m | m | m |  |  | kN | kN
21A | Concrete | Driven (Precast) |  | 6.1 | 9.15 |  |  | -3.05 |  |  | 1.44 | 0.1296 | 0.1296 | Square | 0.36 | 0.36
21B | Concrete | Driven (Precast) |  | 6.55 | 9.15 |  |  | -2.6 |  |  | 1.44 | 0.1296 | 0.1296 | Square | 0.36 | 0.36

## BORE
Pile ID | Time start of Prebore | Time Shaft Bored | Time Base Bored | Time Concreted | Diameter of Bore/outside casing | Bored Pile Remarks | Base or Shaft Grouting Details
PILE_ID | BORE_PRE | BORE_SHAF | BORE_BASE | BORE_CONC | BORE_DIA | BORE_REM | BORE_GRO
ID | yyyy-mm-dd hh:mm | yyyy-mm-dd hh:mm | yyyy-mm-dd hh:mm | yyyy-mm-dd hh:mm | mm

## DRIV
Pile ID | Time to Pre Bore | Time to End of driving/Driving time | Rate of Driving During Installation | Time of cast in place | No. of Blows | Penetration Increment | Driving Shoe Details/Diameter | Base or Shaft Grouting Details | Driven Piles Remarks
PILE_ID | DRIV_PRE | DRIV_TIM | DRIV_INST | DRIV_CAST | DRIV_BLOW | DRIV_PEN | DRIV_SHOE | DRIV_GRO | DRIV_REM
ID | yyyy-mm-dd hh:mm | yyyy-mm-dd hh:mm | mm/min | m |  | mm

## PTST
Pile ID | Test ID | Test loading type | Time from Install (No. of days) | Test rate | Pile Test Remarks
PILE_ID | PTST_ID | PTST_TYPE | PTST_TIM | PTST_RATE | PTST_REM
ID | ID |  | Days | mm/hr
21A | 1 | ML
21B | 1 | ML

## PSLT
PILE ID | Test ID | Load on Load cell 1 | Settlement at Load cell 1 | Time (seconds) | Load cell 2 Depth/Pile Length | Load on Load cell 2 | Settlement at Load cell 2 | Load cell 3 Depth/Pile Length | Load on Load cell 3 | Settlement at Load cell 3 | Load cell 4 Depth/Pile Length | Load on Load cell 4 | Settlement at Load cell 4 | Description
PILE_ID | PTST_ID | PSLT_LOA1 | PSLT_SET1 | PSTL_TIME | PSLT_LOC2 | PSLT_LOA2 | PSLT_SET2 | PSLT_LOC3 | PSLT_LOA3 | PSLT_SET3 | PSLT_LOC4 | PSLT_LOA4 | PSLT_SET4 | PSLT_DESC
ID | ID | kN | mm | Seconds |  | kN | mm |  | kN | mm |  | kN | mm
21A | 1 | 0 | 0
21A | 1 | 199.1899 | 0.00092025
21A | 1 | 391.2482 | 0.58346
21A | 1 | 493.2316 | 1.0011
21A | 1 | 301.6653 | 0.99721
21A | 1 | 103.4336 | 0.21139
21A | 1 | 0 | 0
21A | 1 | 0 | 0
21A | 1 | 387.6933 | 0.87273
21A | 1 | 574.2277 | 1.1597
21A | 1 | 688.174 | 1.3897
21A | 1 | 788.9617 | 1.7611
21A | 1 | 890.7883 | 1.9848
21A | 1 | 987.4964 | 2.5039
21A | 1 | 795.8867 | 2.5062
21A | 1 | 691.1925 | 2.2578
21A | 1 | 593.9322 | 2.2497
21A | 1 | 492.4302 | 1.9799
21A | 1 | 398.1674 | 1.978
21A | 1 | 197.9661 | 1.4722
21A | 1 | 13.196 | 0.502
21A | 1 | 0 | 0
21A | 1 | 0 | 0
21A | 1 | 991.7597 | 2.7625
21A | 1 | 1084.5074 | 2.9798
21A | 1 | 1187.941 | 3.1912
21A | 1 | 1484.91 | 3.9913
21A | 1 | 1480.976 | 4.7669
21A | 1 | 1284.1782 | 3.9935
21A | 1 | 1094.365 | 3.7403
21A | 1 | 886.8163 | 2.982
21A | 1 | 690.9433 | 2.7257
21A | 1 | 487.8527 | 2.1983
21A | 1 | 96.735 | 0.73145
21A | 1 | 0 | 0
21A | 1 | 0 | 0
21A | 1 | 1383.067 | 3.9862
21A | 1 | 1382.8558 | 4.2325
21A | 1 | 1683.2119 | 4.9834
21A | 1 | 1985.8886 | 6.4854
21A | 1 | 1986.4344 | 7.4889
21A | 1 | 1797.8438 | 7.4943
21A | 1 | 1580.9184 | 6.9883
21A | 1 | 1390.8291 | 6.9906
21A | 1 | 1186.3212 | 6.2324
21A | 1 | 990.3996 | 5.7667
21A | 1 | 797.5673 | 5.5104
21A | 1 | 592.9945 | 4.7614
21A | 1 | 392.6902 | 4.4865
21A | 1 | 198.5487 | 3.984
21A | 1 | 7.9353 | 2.9798
21A | 1 | 8.9099 | 2
21B | 1 | 0 | 0
21B | 1 | 100.2403 | 0.19542
21B | 1 | 195.5203 | 0.19765
21B | 1 | 293.9995 | 0.67952
21B | 1 | 395.3884 | 0.68813
21B | 1 | 501.5132 | 1.1764
21B | 1 | 504.7836 | 1.3945
21B | 1 | 292.1045 | 0.98777
21B | 1 | 199.8788 | 0.98872
21B | 1 | 91.2218 | 0.66232
21B | 1 | 12.1901 | 0.51722
21B | 1 | 3.0353 | 0.0062992
21B | 1 | 0 | 0
21B | 1 | 392.4596 | 1.1645
21B | 1 | 504.7836 | 1.3945
21B | 1 | 604.909 | 1.6086
21B | 1 | 802.6086 | 2.2018
21B | 1 | 895.2224 | 2.3877
21B | 1 | 994.7736 | 2.6952
21B | 1 | 993.2668 | 3.1903
21B | 1 | 800.4317 | 2.8058
21B | 1 | 591.4304 | 2.8009
21B | 1 | 399.6619 | 1.993
21B | 1 | 295.1421 | 1.9937
21B | 1 | 103.8821 | 1.6031
21B | 1 | 0.23749 | 1.2114
21B | 1 | 0 | 0
21B | 1 | 688.2227 | 2.5572
21B | 1 | 886.4827 | 3.3092
21B | 1 | 990.1466 | 3.6978
21B | 1 | 1097.5784 | 4.2235
21B | 1 | 1197.4688 | 4.2258
21B | 1 | 1285.5489 | 4.3991
21B | 1 | 1493.7762 | 5.0299
21B | 1 | 1293.9572 | 5.0315
21B | 1 | 1099.0494 | 4.7342
21B | 1 | 902.3805 | 4.7234
21B | 1 | 708.583 | 4.2455
21B | 1 | 496.1144 | 3.8045
21B | 1 | 311.997 | 3.2522
21B | 1 | 106.269 | 2.7148
21B | 1 | 9.2117 | 2.2517
21B | 1 | 0 | 2
21B | 1 | 0 | 0
21B | 1 | 859.0888 | 3.265
21B | 1 | 1018.6944 | 3.8043
21B | 1 | 1394.2932 | 5.2113
21B | 1 | 1494.4761 | 5.4161
21B | 1 | 1593.989 | 5.7298
21B | 1 | 1696.9636 | 6.2305
21B | 1 | 1793.7804 | 6.2328
21B | 1 | 1902.514 | 6.5467
21B | 1 | 2001.2474 | 7.2372
21B | 1 | 2003.7192 | 7.8352
21B | 1 | 1593.4003 | 7.8256
21B | 1 | 1396.089 | 7.4192
21B | 1 | 1194.4215 | 7.2214
21B | 1 | 203.0714 | 4.7194
21B | 1 | 0 | 3.7

## CTST
TEST_ID | Pile ID | Type of test/Size | Test age | Strength | Remarks
CTST_ID | PILE_ID | CTST_TYPE | CTST_AGE | CTST_STRN | CTST_REM
ID | ID | mm | Days | kPa

## CYCL
PILE ID | Test ID | Cycle No. | Qmin | Qmax | Duration of respective cycling between Qmin and Qmax Time (mins) | Cumulative number of cycle repetitions (n) | Total Settlement over duration of repetitive cycling (mm) | Description
PILE_ID | PTST_ID | CYCL_CYC | CYCL_LOA1 | CYCL_SET1 | CYCL_TIME | CYCL_REP | CYCL_SET1 | PSLT_DESC
ID | ID |  | kN | mm | Minutes |  | mm